PAGE  
AlertWave – Wireless Emergency Mass Notification and Personnel Alert System Specifications


Visiplex, Inc.

1287 Barclay Boulevard

Buffalo Grove, IL 60089
877-918-7243
www.visiplex.com

Product Guide Specification (08/2011)
	This product specification is written according to the Construction Specifications Institute (CSI), MasterFormatTM, SectionFormat, and PageFormat, contained in the CSI Manual of Practice.


WIRELESS EMERGENCY MASS NOTIFICATION SYSTEM
Part 1 - General
	Specifier Note:  Edit the following list as required for the project.


1.1  Sections Included
A. Transmission System
1. Primary Control Center PC with Microphone.
2. Primary External Transmitter.
B. Wireless Notification and Mass Alert Devices 
1. Wirelessly Controlled Public Address Speaker.
2. Wirelessly Controlled Strobe Light.
3. Wirelessly Controlled Alphanumeric LED Display.
4. Wirelessly Controlled Siren.
	Specifier Note: Edit the following list as required for the project. List other sections with work directly related to this section.


1.2  Related Sections
A. Division 16 - Electrical 120V grounded outlet required for encoder.

B. Division 16 - Electrical 120V 60Hz grounded outlet required for external transmitter.

C. Division 16 – Electrical 120V 60Hz grounded outlet for each AC powered wirelessly controlled public address speaker, strobe light, alphanumeric LED display and sirens. 

	Specifier Note: List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards and is merely a list of those used.


1.3 References
A. This Technical Specification and Associated Drawings.

B. National Fire Protection Agency (NFPA) 72, National Electric Code 2010.

C. Visiplex, Inc. AlertWave Wireless Mass Notification System User Manual.

1.4 System Description
A. Wireless Emergency Mass Notification system shall activate and wirelessly control remote alerting devices such as PA speakers, strobe lights, LED displays and siren horns.
B. The main system shall include a dedicated microphone, full keyboard for data entry, serial connections to in-house alert system, serial connection to optional building automation systems, software and hardware interface for network access, FCC approved transmitter and a UPS power backup.
C. The main system shall be capable of sending alerts to the following devices:

1. Wirelessly Controlled PA Speakers: Activation of embedded tones and bells, pre-recorded voice alerts and user recorded voice alerts.
2. Wirelessly Controlled Strobe Lights: Activation of devices that have ON and OFF status, including strobe lights and sirens.
3. Wirelessly Controlled Alphanumeric LED Display: Activation of alphanumeric displays that can display an alphanumeric message using different formats and effects.
4. Wirelessly interface with local Fire Alarm system by providing dry-contact control and PA audio signal. 
5. Wireless Pagers: Activation of alphanumeric, numeric, tone-only and voice pocket pagers.
6. Email Notification: Sending email messages to email subscribers.
7. Audio Output: activation of voice alerts that may be played thorough the PC audio output and activation of voice alerts that may be played thorough the telephone line.
8. Network Notification: Sending alphanumeric alerts to Client software users.
9. Modem Dial Out: Sending alphanumeric alerts to pagers and cell phones that are capable of receiving messages using a 3rd party provider using TAP protocol via modem connection.
D. The system shall be capable of generating user attended alerts using the following interfaces:

1. Dialing in to the telephone line connected to the main system and following the system’s prompts.
2. Using PC software that allows network users to send audible, visual and alphanumeric messages from their PC.
E. The system shall be capable of generating automated alerts using the following interfaces:

1. Dry-contact closure of one of the alarm / dry-contacts.

2. Incoming serial data, which will be processed according to the active protocol on the specific serial port receiving the data.
3. Triggering a button or dry-contact closure of a 900MHz wireless transmitter or wireless push button.
4. Receiving an email message that may be forwarded to a specific device or analyzed according to the Data Stream Analyzer protocol for conditional messaging.
5. Pre-programmed scheduled events that may activate individual or multiple wireless and non-wireless devices.
F. The main system shall provide a graphic Visual Control Panel for monitoring dry-contact alarm inputs and wireless push buttons and transmitters and activation of alerts, allowing placement of visual indicators over a site map or any other image.

G. The main system shall archive all system activity with date and time for on-demand reports. 

H. The main system shall be capable of accessing wireless devices and non-wireless devices individually and as a group, including groups of devices of different types.

I. The main system shall be capable of supporting 10000 devices, 1000 pre-recorded voice messages, 1000 dry-contact alarm inputs, 1000 wireless push button and transmitters, 1000 “keywords” for conditional messaging and 250 RS232 serial ports.
J. The system shall be capable of providing a “Secure Mode” design so that no other paging transmitter can activate the local wireless remote devices. The “Secure Mode” code should be programmable from the system main console.
K. The system shall be capable of providing an “Over-the-Air” programmability design. This feature shall allow programming wireless remote devices (such as wireless remote devices such as speakers, strobe lights, LED displays and sirens) into groups/zones and setting their operation mode wirelessly from the system main console.
L. The system shall be capable of providing full supervision capabilities of all system wireless remote devices such as speakers, strobe lights, LED displays and sirens. This feature shall allow each remote wireless device to report back its operational status, setup information and internal battery status upon wireless request from the main system.
M. The main system shall provide a voice gateway to access wirelessly controlled PA speakers individually or as a group. Real-time voice messages can be initiated via the system microphone or the telephone line interface. The messages may be initiated automatically or manually by the user.
N. The main system shall provide an “Alert Tone” voice gateway to access wirelessly controlled PA speakers individually or as a group. The messages may be initiated automatically or manually by the user.

O. The main system shall support activation of wirelessly controlled strobe lights individually or as a group. The messages may be initiated automatically or manually by the user.

P. The main system shall support activation of wirelessly controlled alphanumeric data displays individually or as a group. The messages may be initiated automatically or manually by the user.
Q. The main system shall support activation of wirelessly controlled siren horns individually or as a group. The messages may be initiated automatically or manually by the user.

R. The wirelessly controlled PA speakers shall include storage of at least 8 pre-recorded voice messages or alert tones. The wirelessly controlled PA speakers shall be capable of being a member of at least 8 groups or zones, with a built-in real time clock and full wireless programmability.
S. The wirelessly controlled strobe lights shall be capable of being a member of at least 8 groups or zones, with full wireless programmability.
T. The wirelessly controlled alphanumeric LED displays shall be capable of wirelessly receiving alphanumeric text messages from the main system and display them in 1 to 4 lines (model dependent). The wirelessly controlled alphanumeric LED displays shall be capable of being a member of at least 6 groups or zones.
U. The wirelessly controlled siren horn shall be capable of being a member of at least 8 groups or zones, with full wireless programmability.
V. The wirelessly controlled speaker, strobe light, alphanumeric display or siren horn shall be capable of supporting built-in battery backup.

W. The system shall incorporate a “fail-safe” design so that a temporary power interruption shall not cause failure of the entire system. Upon restoration of power, the system shall resume normal operation without the need to reset the system or any of its components.
X. The system shall include a notification pager to automatically notify a local supervisor or maintenance personnel of any system malfunction within seconds.
1.6 Regulatory Requirements
A. Equipment and components furnished shall be of manufacturer’s latest model.
B. The system layout should comply with the NFPA72, 2010 guide for planning and implementation of a Emergency Notification System.
C.
Encoder, transmitter and receivers shall comply with Part 90 of FCC rules, as follows:

1. This device may not cause harmful interference.
2. This device must accept interference received, including interference that may cause undesired operation.
3. Transmitter frequency shall be governed by FCC Part 90.35.
4. Transmitter output power shall be governed by FCC Parts 90 and 74.

D.
System shall be installed in compliance with local and state authorities having jurisdiction.

1.7  Submittals
	Specifier Note:  In accordance with FCC regulations, an application for license must be filed prior to use of the equipment.  Normally, the manufacturer will complete the filing and obtain the license on the behalf of the Owner. 

Otherwise, the Owner will be required to file the application with the FCC prior to use.  Furnishing the license, or a copy of the application, will confirm that FCC approval has been obtained.


A. Product Data: Submit complete catalog data for each component, describing physical characteristics and method of installation. Submit brochure showing available colors and finishes of PA amplifiers and speakers, strobe light controllers and strobe light lens, LED displays and sirens.
B.
Operating License: Submit evidence of application for operating license prior to installing equipment.  Furnish the license, or if the license has not been received, a copy of the application for the license, to the Owner prior to operating the equipment. When license is received, deliver original license to Owner.
C.
Manufacturer's Instructions: Submit complete installation, set-up and maintenance instructions. 
1.7 Substitutions
A.
Proposed substitutions shall be manufactured of equivalent materials that meet or exceed specified requirements of this Section.

B.
Proposed substitutions shall be identified not less than 10 days prior to bid date. 

C.
Systems requiring wiring and/or conduit between the system controller and the remote devices (such as PA amplifiers and speakers, strobe light controllers and strobe lights, LCD displays or sirens) or the remote devices controller will not be acceptable.

1.8  Quality Assurance
A. Permits: Obtain operating license for the transmitter from the FCC (service may be provided by Visiplex).


B.  Qualifications:

1.
Manufacturer: Company specializing in manufacturing commercial wireless systems with a documented experience of minimum of 10 years.
2.
Installer: Company with documented experience in installation of commercial wireless systems. 
1.9 Delivery Storage and Handling
A.
Deliver all components to the site in the manufacturer's original packaging.  Packaging shall contain manufacturer's name and address, product identification number, and other related information.

B.
Store equipment in finished building, unopened containers until ready for installation.

1.10 Project Site Conditions
A.
Wirelessly controlled devices and shall not be installed until painting and other finish work in each room is completed.

B. Coordinate installation of the external antenna (if used) for access to the roof or exterior side-wall so that the bracket and related fasteners are watertight.

Part 2 – Products
	Specifier Note:  Select from the following product list all the products and options that fit your system design. Consult Visiplex for additional information regarding product features and options.


2.1 Manufacturer
A. Wireless Emergency Mass Notification and Public Address system and its components shall be manufactured by Visiplex:
Visiplex, Inc.

Buffalo Grove, IL 60089
Tel: 877-918-7243

Website: www.visiplex.com
2.2 System Operations and Startup Sequence
The VNS5100 AlertWave system is a powerful multitasking PC that is capable of sending both pre-programmed and real-time voice messages to specific PA speakers or designated groups of PA speakers.  This message can be generated over the phone using the system’s telephone interface, or generated through the system’s microphone.  The VSN5100 is also capable of wirelessly controlling a number of alert devices, such as strobe lights, siren horns and alphanumeric pagers.  Capabilities also include the ability to send a text message to an alphanumeric LED displays as a result of a preprogrammed event or a message that was generated from the PC keyboard or a network client. The VNS5100 can also initiate mass e-mail and phone messaging to predefined personnel and occupant lists. 
A.
Control Center Operation:  
When power is first applied to the unit, it will start the Windows boot process.  Once the software is fully loaded, the main control screen is displayed and the system is ready for operation.
B.
Wireless PA Speaker Operation:  
· Connect the DC adaptor (supplied with each wireless amplifier) to AC power source.

· After few seconds of initial setup, the wireless amplifier LED will start flashing to indicate that all the internal circuitry is fully functioning.

· Connect a speaker to the wireless amplifier speaker output port using the supplied cable. The speaker is now ready to receive voice and data information from the main control center. 

C.  Wireless Strobe Light or Siren Operation:  

· Connect the DC adaptor (supplied with each wireless controller) to AC power source.

· After few seconds of initial setup, the wireless controller LED will start flashing to indicate that all the internal circuitry is fully functioning.

· Connect a strobe light or siren to the wireless controller output port using the supplied cable. The device is now ready to receive wireless activation commands from the main control center.
D.  Wireless Alphanumeric Data Display Operation:  
· Connect the DC adaptor (supplied with each display) to the AC power source. 
· After few seconds, the alphanumeric display will scroll an activity status line on the display, to indicate that all internal parts are working properly. After few more seconds the display will be cleared until it receives new information to be displayed transmitted from the main control center.
2.3 Equipment
	Specifier Note: Select the encoder with features as needed. Select suitable transmitter to provide full coverage facility wide. In general, use an internal transmitter for single building and an external more powerful transmitter for larger facilities.


A. General: 
The basic mass notification system shall include a control center, an external transmitter and any combination of controlled devices like wireless PA speakers, wireless strobe lights, wireless LED displays and wireless siren horns.  
B. Encoder: 
Visiplex model VNS5100 shall incorporate a PC, keyboard and a microphone to provide the following features:
1. Send voice messages to any wirelessly controlled remote speakers or groups of speakers (zones), activate embedded alert tones on wirelessly controlled remote speakers, activate and deactivate wirelessly controlled strobe light and siren horns, send alphanumeric text messages to LED displays, send alphanumeric text messages to email subscribers, send alphanumeric text messages to pagers, send voice message to telephone or cell phone subscribers,
2. Password protected Administrator login to set individual and group addresses and other parameters for remote wireless devices and non-wireless devices, database programming and activity reports generating.
3. Database programming and administration.
4. Remote access via telephone interface for voice and alphanumeric messaging.
5. Ethernet interface for network access.
C. Transmitter: 
Visiplex model VTX-6 or VS101-xxx series transmitter with up to 300 watts. The transmitter parameters shall be:

1. Frequency Range: 148-174 MHz or 401–470 MHz.
2. Transmitter output power: Internal 6 watt (built into the encoder) or External 25-300 watt in black metal case (14.125” by 11.625” by 3.375”).
3. Transmission Range: Up to 15 miles radius (transmitter and antenna depended).
4. Radio technology: Narrowband FM, 12.5KHz bandwidth.

5. Transmission format: POCSAG, digital one-way communication.
6. Digital Data rate: 512 BPS.
7. Operating range: 0-70 degrees Celsius.

D. Antenna: 
Visiplex model VS638 (indoor), or model VS654 (outdoor) or model VS655 (outdoor). Antenna polarization shall be vertical.

E. Power supply:
Included with encoder.

F. Surge Protector/Battery Backup:
Visiplex model VS56900.

Input:  120-volt AC 60 Hz +/- 1 Hz.

Output: 120-volt AC, 1500VA, 950-watts

Surge Energy Rating: 1800 joules

G. Wirelessly Controlled PA Speakers:
Visiplex model VNS2200, Indoor/Outdoor Wireless Controller. Overall dimensions: 7.5” long by 5.1” wide by 2.7” deep.

The wireless amplifier shall be connected to 4-16 Ohm Ceiling-Mount, Wall –Mount or Horn speakers Visiplex model VNS2081, VNS2082, VNS2083, VNS2084 or VNS2085. The speaker may have a polycarbonate or metal enclosure.  Overall dimensions of speakers shall be:

VNS2081: 8.1” diameter by 2.8” deep
VNS2082: 7.3” wide by 9.8” high by 6.5” deep
VNS2083: 8.6” wide by 12” high by 7.8” deep
VNS2084: 11.25” wide by 8.2” high by 11.1” deep
VNS2085: 16.9” wide by 10.8” high by 14.1” deep
	Specifier Note: For other models with other amplifier and speaker power, indoor/outdoor, color and case style select from Visiplex brochure or website.


1. Wireless PA speaker shall be able to receive voice messages, alert tone activation, programming commands and be controlled from the VNS5100 control center.
2. Power source: 100-240 VAC, 50-60 Hz.
3. The PA speaker shall have four levels of volume control selectable and controlled by the system control center.

H. Wirelessly Controlled Strobe Light: 
Visiplex model VNS2200, Indoor/Outdoor Wireless Controller. Overall dimensions: 7.5” long by 5.1” wide by 2.7” deep.

The wireless controller shall be connected to a strobe light Visiplex model VNS2091 to VNS2094. The strobe light shall have a polycarbonate enclosure. Overall dimensions: 4.25” diameter by 2.25” deep.

	Specifier Note: For other models with other lens style, colors, and case styles select from Visiplex brochure or website.


1. Wireless Strobe Light device shall be activated and deactivated wirelessly from the VNS5100 system.
2. Power source: 12VDC, 1A using 100-240 VAC, 50-60 Hz power adapter.
I. Wirelessly Controlled Alphanumeric Displays:

Visiplex model VNS2200, Indoor/Outdoor Wireless Controller. Overall dimensions: 7.5” long by 5.1” wide by 2.7” deep.

The wireless controller shall be connected to a 16 characters, 2-line Wireless Alphanumeric Data display Visiplex model VS1512. The display shall have metal or polycarbonate enclosure and polycarbonate lens. Text LED color shall be red. Overall dimensions: 26.52” long by 6.75” by 2.5” deep.

	Specifier Note: For other models with other digit style, colors, and case styles select from Visiplex brochure or website.


1. Wireless Alphanumeric Display shall be able to receive time and data information from the VNS5100 control center.
2. Power source: 100-240 VAC, 50-60 Hz.
3. Alphanumeric display shall be viewable from 100 feet or more.

J. Wirelessly Controlled Siren:
Visiplex model VNS2200, Indoor/Outdoor Wireless Strobe Light Controller. Overall dimensions: 7.5” long by 5.1” wide by 2.7” deep.

The wireless controller shall be connected to two-tone siren Visiplex model VNS2086. The siren shall have a polycarbonate enclosure. Overall dimensions: 4” long by 4” wide by 3.5” deep.

1. Wireless Siren device shall be activated and deactivated wirelessly from the VNS5100 system.
2. Power source: 12VDC, 1A using 100-240 VAC, 50-60 Hz power adapter.

Part 3 – Installation
3.1 Site examination:
A. Verify that construction is complete at installation locations and that rooms are clean and dry.

B. Verify that 120-volt electrical outlet is located within 6 feet of location of transmitter and the outlet is operational and properly grounded.

C. Verify that all 120-volt electrical outlets for the wirelessly controlled speakers, strobe lights, alphanumeric displays and siren are located at the exact installation point and that the outlet is operational and properly grounded.
3.2 System Installation: Refer to the manufacturer installation manuals as supplied with the system and install each one of the system components.
3.3 Inspection: Prior to final acceptance, inspect each system component for proper function and replace parts that are found to be defective.
3.4 Cleaning: Prior to final acceptance, clean exposed surfaces of all system components, using cleaning methods recommended by the manufacturer. Remove temporary protective film from display lenses.
3.5 Delivery: Provide training to Owner's representative on system setting and operation as demonstrated in the manufacturer system user manual.
PAGE  
6
Copyright © 2011 Visiplex, Inc. - All Rights Reserved


